## Sheet1
GENERAL CHECKLIST FOR LIFT INSTALLATIONS (JOB NO. )
Sl No | Description | Yes | No | Remarks
1 | Whether permanent supply upto the dedicated Main Switch/MCCB for lift is available
2 | Whether separate & dedicated single phase main switch/MCCB has been provided for lift shaft light
3 | Whether lift main switch provided at nearest convenient location in lift loby
4 | Whether the Lift Main Switches at Ground Floor have been earthed with 8 SWG G.I wire at two distinct points
5 | Whether main switch earthings are done to the building earth bar
6 | Whether building earth bar is connected with minimum two earth pits and those are properly marked as earth pits
7 | Whether earth resistance at building earth bar measured & is within acceptable limit
8 | Whether proper marking on lift main switch done
9 | Whether civil jobs at each floor lift landing positions completed
10 | Whether each landing has a proper lift loby with fire exit
11 | Whethet staircase hand rail/guard at each floor provided
12 | Whether staircase hand rail for machine room provided
13 | Whether pit is cleaned and water proof
14 | Whether pit stop switches are available
15 | Whether Pit light is working
16 | Whether pit ladder is provided
17 | Whether Shaft lights are working
18 | Whether limit switches earthing done
19 | Whether buffer foundations are properly done with R.C.C
20 | Whether lift loby lights are provided at each floor
21 | Whether cwt clamping or tie split pins provided
22 | Whether counter guard net provided upto required height
23 | Whether toe guard of minimum 750 mm provided
24 | Whether proper pit depth maintained as per IS 14665
25 | Whether proper cwt run-by maintained as per IS 14665
26 | Whether proper bottom clearance maintained as per IS 14665
27 | Whether landing gate seal gap checked & found ok
28 | Whether Facia for automatic door provided
29 | Whether finishing done below the landing door seal for manual door
30 | Whether car ligts are kept direct
31 | Whether alarm bell checked and found ok
32 | Whether all LEDs of floor indicator etc are working
33 | Whether all lights, fan inside car are working
34 | Whethet gate locks at each floor checked & found ok
35 | Whether proper top clearance maintained as per IS 14665
36 | Whether machine room door is outside opening and made of Fire Proof/weather proof as per IS 14665
37 | Whether metal 415 V danger plate outside machine room door provided
38 | Checked for any water ingress source to machine room through window, exhaust etc
39 | Machine room main switch properly earthed at two distinct points with 8 swg G.I
40 | Whether proper light & ventilation in machine room provided
41 | All earthing wires, controller wiring etc are properly dressed
42 | Lift machine properly installed & fastner bolt provided
43 | Whether rope end are properly sealed
44 | All limit switches( up/down final, governor safety) installed at requisite location
45 | Whether Governor name plate with tripping speed fixed on governor body
46 | Whether extra cut-out on machine room floor has been properly covered
47 | Whether UP & Down final limit checked & found ok
48 | Governor safety (both electrical & mechanical) checked and found ok
49 | Whether load balancing checked & found in order
50 | Load test(if done on the hook at machine room) has been tagged
51 | Whether governor switch and car safety switch or both the switches are manually operable
52 | Whether Governor actuation facility from control panel provided for MRL lift
53 | Whether Manual Rescue Device provided for MRL Lift
54 | Whether controller maintenance access panel besides top floor landing for MRL Lift
55 | Whether separate brake contactor provided in case of Metal/metal contact
56 | Whether clear laminated safety glass used & certificate available in case of glass lift/shaft
57 | Whether dynamic brake incorporated in case of drive
58 | Whether cover for the dynamic resistance provided in case of installation outside panel

## Sheet2
245000

## Sheet3
A
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z